## Sheet1
From-To | R (Ω) | R(p.u) | X (Ω) | X(p.u) | MVA Rating | From-To | R (Ω) | R(p.u) | X (Ω) | X(p.u) | MVA Rating
1-2 | 13.225 | 0.025 | 52.9 | 0.1 | 75 | 2-6 | 26.45 | 0.05 | 105.8 | 0.2 | 72
1-4 | 26.45 | 0.05 | 105.8 | 0.2 | 72 | 3-5 | 26.45 | 0.05 | 105.8 | 0.2 | 72
1-5 | 26.45 | 0.05 | 105.8 | 0.2 | 72 | 3-6 | 26.45 | 0.05 | 105.8 | 0.2 | 72
2-3 | 13.225 | 0.025 | 52.9 | 0.1 | 75 | 4-5 | 13.225 | 0.025 | 52.9 | 0.1 | 75
2-4 | 26.45 | 0.05 | 105.8 | 0.2 | 72 | 5-6 | 13.225 | 0.025 | 52.9 | 0.1 | 75
2-5 | 26.45 | 0.05 | 105.8 | 0.2 | 72
Power Base | 100 | MVA |  | Given Color
Voltage Base | 230 | kV |  | From Power World
Zbase | 529 | Ω |  | Calculated

## Sheet2
Voltage Control + Slack Bus |  |  | Load Bus |  |  | Line losses
Bus # | Real Power (MW) | Reactive Power (MAR) | Bus # | Real Power (MW) | Reactive Power (MAR) | Real Power Loss (MW) | Reactive Power loss (MAR)
1 | 150 | 57 | 4 | 95 | 75 | 10 | 39
2 | 65 | 121 | 5 | 90 | 70 | % (MW) loss | % (MVAR) loss
3 | 65 | 71 | 6 | 85 | 65 | 3.571% | 15.66%
Total Power Produced | 280 | 249 | Total Power Absorbed at Load Bus | 270 | 210

## Exp1
New Line Status |  | Lines in Orange Status | Lines above 70%
1-6 | 3-4
Off | Off | 1-4 in Orange Status
Off | On | None | 1-4 and 1-5 | Line 1-4 75% and Line 1-5 is 77%
On | Off | None | 1-4 | Line1-4 is 79%
On | On | None | None

## Exp2
Shunt Status by Bus |  |  | Lines in Orange Status
4 | 5 | 6
Off | Off | Off | 1-4
Off | Off | On | 1-4 | Down to 86%
Off | On | Off | 1-4 | Down to 85%
Off | On | On | 1-4 | Down to 83%
On | Off | Off | 1-4 | Down to 80%
On | Off | On | None | Down to 79%
On | On | Off | None | Down to 78%
On | On | On | None | Down to 77%

## Exp3
Line Name | MVA | MVA (p.u) | V1 (p.u) | V4 (p.u) | V(1-4)
1-4 |  |  | 1.05 | 0.952 | 0.098
1-5 |  |  | 1.05 | 0.968 | 0.082
Base MVA | 100